SECTION 26 28 13 fuses 600 volt

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - This Section specifies the requirements for 600V fuses rated 0-600 amps and rated 601-6000 amps.

      - REFERENCE STANDARDS

        - The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

        - All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

        - All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references:

          - ANSI/UL 198E - Class R Fuses.

          - ANSI/UL 198C - High Interrupting-Capacity Fuses, Current Limiting Types, Class L.

          - ANSI/NEMA FU 1 - Low Voltage Cartridge Fuses.

          - ANSI/UL 248 - Fuses.

      - SUBMITTALS

        - Product Data:

          - Submit manufacturer’s data on fuses.

      - Extra materials

        - Refer to Section 01 78 46 for Maintenance Material Requirements.

- PRODUCTS

      - GENERAL

        - All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

      - MANUFACTURERS

        - Eaton/Bussman.

        - Ferraz Shawmut.

        - Littelfuse.

        - Low voltage fuses must be products of a single manufacturer.

      - MATERIAL AND EQUIPMENT

        - Furnish fuses in accordance with the following:

          - Motors and Transformers, 0 to 600 amp:

            - 250 volt - Buss LPN-RK, UL Class RK1.

            - 600 volt - Buss LPS-RK, UL Class RK1.

          - Lighting Loads, 0 to 600 amp:

            - 250 volt - Buss LPN-RK, UL Class RK1.

            - 600 volt - Buss LPS-RK, UL Class RK1.

          - All applications, 601 to 6000 amp:  600 volt - Buss KRP-C, UL Class L.

        - Size fuses serving motor loads actually installed as specifically recommended by motor or equipment manufacturer or 125 percent of motor nameplate rating, or the next standard.

        - Interrupting Rating:  200,000 RMS amps.

- EXECUTION

      - SPARE FUSES

        - As spares, provide the greater amount of either three fuses or 10 percent of each size and type installed.    Refer to 01 79 00- Demonstration & Training and 01 78 46- Maintenance Materials.

      - INSTALLATION

        - Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

        - All installation shall be in accordance with manufacturer’s published recommendations.

        - Fuse Clips.  Check fasteners on fuse clips for tightness when installing fuses.

        - Labels.  Install fuses so label is in an upright, readable position. Fuses without labels are not acceptable.

END OF SECTION 26 28 13