Electrical System Testing Procedures

System Verification and Functional Performance Test Flow Chart

NORMAL POWER					EMERGENCY POWER				DISTRIBUTION

Submittal Approval

Submittal Approval

Shop / Coordination Drawing Approval

MSB / Switchgear Installation (EC)

Raceway Wiring and Terminations

Install Bus Duct, Raceway, Wiring, Rough-in Boxes,

Transformers, Panels, Grounding and Bonding (EC)

Gensets / Switchgear / ATS Installation (EC)

Raceway Wiring and Terminations

Inspections (MDA)

Inspections (MDA)

Inspections (MDA)

Cable / Component Resistance Testing (EC)

Cable / Component Resistance Testing (EC)

Cable / Component Resistance Testing (EC)

PASS

Electrical Testing Agency

NETA Testing

Witness by MDA / CxA

Contractor

Corrects

Deficiency

NO

Electrical Testing Agency

NETA Testing

Witness by MDA /CxA

Electrical Testing Agency

NETA Grounding Testing

Witness by MDA / CxA

PASS

Issues noted in

ISU Log

NO

Permanent Power / Architectural Finishes Complete

NO

YES

Electrical Trim out (EC)

(Inspections by MDA)

Contractor and Subs perform pre-startup inspections and document on PFC’s;

PFC’s submitted to CxA for Review

Contractor and Subs perform pre-startup inspections and document on PFC’s;

PFC’s submitted to CxA for Review

Contractor and Subs perform inspections and document on PFC’s; Completed PFC’s submitted to CxA for Review

Contractor Corrects Issues

Contractor issues Request for Startup to MDA

Contractor issues Request for Startup to MDA

Equipment Startup

APPROVED

Generator / Paralleling Gear Startup

NO

Issues noted in

ISU Log

YES

APPROVED

FUNCTIONAL PERFORMANCE TESTING

(CxA, Contractor, MDA)

PASS

INTEGRATED

SYSTEMS TEST

(CxA, Contractor, MDA)

SUBSTANTIAL COMPLETION

DEFERRED / LOAD TESTING

(THERMAL)

PERMANENT POWER

TO FACILITY

ATS / UPS Startup

APPROVED

Pass

Pass

Pass

Pass

Pass

PASS

Completed PFC’s and startup documentation submitted to

CxA for Review

YES

Issues noted in

ISU Log

NO

BAS Graphical Interface Complete

BAS Graphics Approved by AFCO

IT Connectivity Complete;

BAS Online

Contractor and Subs perform pre-test of systems using FPT procedure

Contractor issues Request for Functional Performance Testing to MDA

NO

Issues noted in

ISU Log

Contractor Corrects Issues

YES

WARRANTY PERIOD

Completed PFC’s and startup documentation submitted to

CxA for Review

YES

NO

Contractor Corrects Issues

Issues noted in

ISU Log

BAS Point Verification

(CxA, Contractor, MDA AFCO)

Glossary:

AFCO	Administrative Facilities and Campus Operations

ATS 		Automatic Transfer Switch

BAS		Building Automation System

CxA		Commissioning Authority

EC		Electrical Contractor

FPT		Functional Performance Test

ISU		Issues Log

IT 		Information Technology

MDA 	MD Anderson

NETA	National Electrical Testing Association

PFC 	Prefunctional Checklist

YES

NO

Issues noted in

ISU Log

Contractor Corrects Issues

YES

NO

Issues noted in

ISU Log

Contractor Corrects Issues

YES

NO

Issues noted in

ISU Log

Contractor Corrects Issues

YES

NO

Issues noted in

ISU Log

Contractor Corrects Issues

YES

NO

Issues noted in

ISU Log

Contractor Corrects Issues

YES

NO

Issues noted in

ISU Log

Contractor Corrects Issues